## Sheet1
Hosting of eFEAP Next Infrastructure in Co-location Data Center
RFP Ref: LIC/CO/IT-SD/EFEAP-NEXT/COLOCATION/19-20/01 Dated: 08/07/2019
Bidder's Name:
CO-Location Centre
SL No. | Certification | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details/link of Proof Attached
1 | The bidder proposed site should have following compliance / certifications: |  |  | 33 | Letter / Certificate from the certified agency.
a. | NFPA 70 & 75 |  | 3
b. | IS 1893:1984 seismic Compliance |  | 2
c. | TIA 942 compliance (Tier III Infrastructure) 3 marks |  | 5
TIA 942 compliance (Tier IV Infrastructure) 5 marks
d. | PCI DSS |  | 2
e. | ISO 20000 |  | 3
f. | ISO 9001 |  | 3
g. | Compliance to ASHRAE Standards |  | 3
h. | ISO/IEC 27001 |  | 3
i. | Uptime Tier III (Infrastructure) 3 marks |  | 5
Uptime Tier IV (Infrastructure) 5 marks
j. | ISAE3402 |  | 2
k. | TVRA(Threat and Vulnerability Assesment) |  | 2
2 | The structural strength of the proposed building should have been certified and latest report to be available. The report should not be more than one year old. ( Copy of report/ certificate to be attached.) |  |  | 2 | Copy of report / certificate to be attached
| Total |  |  | 35
| Functional Specifications | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
3 | The bidder must be the owner of the proposed Data Center provided to LIC or in case of leased premises, an unexpired lease period must be for 12 years from the RFP Response due date. |  |  | 5 | Relevant documents to be attached
4 | Age of the Building |  |  | 5
a. | Less than 5 years |  | 5
b. | > 5 years but < = 10 years |  | 3
c. | >10 years but < = 15 years |  | 2
5 | The Proposed Data Center building should not be in low lying and flood prone area |  |  | 3
6 | The Data Center should have a load bearing capacity of minimum 1000 Kg/ Sqmtr. |  |  | 5
a. | > 1450 kg/sqmtr |  | 5
b. | > 1200 and < 1450 kg/sqmtr |  | 4
c. | >1000 but <1200 kg/sqmtr |  | 3
d. | >900 and <1000 kg/sqmtr |  | 2
7 | The caged area for LIC within Data Center should have enough contiguous space to host minimum 40 racks . |  |  | 5 | Self Declaration and evaluation during site visit
8 | The Server Room Area should have raised floor height of 2.5 ft |  |  | 2 | Relevant documents to be attached
9 | The server hall height from raised floor to false ceiling should be at least 14 ft. |  |  | 3
10 | Freight Lift - The data center should have high capacity freight lift for ease of movement of servers and high-density network devices |  |  | 5 | Self Declaration and evaluation during site visit
11 | A separate Cage dedicated for LIC within the server room / Server Hall area |  |  | 3 | Self Declaration
12 | The Data Center should have microprocessor based system to detect water leakage within reasonable period of time to avoid any related damage |  |  | 3 | Relevant documents to be attached
13 | The Data Center should have electronic rodent control systems with operability on varied frequency range |  |  | 2
14 | The building & Server cabin area should be provided with Water Leak Detection System and fire alarm system |  |  | 2
15 | IF proposed colo site's DC uptime is between 99.982% and 99.99% both inclusive |  | 10 | 15 | Relevant reports to be attached
| IF proposed colo site's DC uptime is more than 99.99% |  | 15
16 | Feeds should be provided to LIC for monitoring the cages/its infrastructure remotely. |  |  | 3 | Self Declaration
17 | Gate Passes to enter SP’s premises for LIC’s representatives – free of any cost |  |  | 3 | Relevant reports to be attached
18 | Audit reports of people accessing the Server room should be available as and when required by LIC. |  |  | 3 | Self Declaration
19 | The Data Center building should be designed and constructed for earthquake resistance and should be away from hazardous chemical materials, LPG storage areas, chemical go-downs and other storage facilities meant for dangerous commodities. |  |  | 3 | Relevant reports / documents to be attached and evaluation at site visit
20 | Vendor to certify that Data Center is adequately distant from this site to major manufacturing, industrial, or utility areas that may cause power instability, radio frequency interference, pollution, vibration, etc. |  |  | 3 | Relevant reports / documents to be attached and evaluation at site visit
21 | Arrangement (for seating, power and network) should be made to LIC’s team of around 10 people in disaster situation to access systems hosted in DC. |  |  | 2 | Self Declaration
22 | Should be in DC operating business for a minimum period of 5 yrs |  |  | 2 | Relevant documents to be attached
23 | The proposed building should be covered under comprehensive insurance on ongoing basis including risk related to earthquake, floods, fire, lightening, terrorist attacks etc. (Copy of last year and current year) |  |  | 2
24 | Air Quality in the data center site should be of severity level G1 (mild) as per ISA -71.04. |  |  | 5
25 | The seating area should include the desk, chair, drawer which can accommodate three box files with locking facility per seat, UPS power connections (three per seat), network connections from LIC’s server area / LAN (two per seat) etc. Vendor shall factor sufficient work area per seat. Inaddition, vendor shall provide adequate space for the movement within the enclosed seating area. |  |  | 5 | Self Declaration
26 | The bidder should provide staging /storage area for two to three weeks. |  |  | 2 | Self Declaration
27 | Staging area should be in the same floor, preferably close to the hired / hosted space and have all facilities like, redundant power,LAN connectivity, telecom |  |  | 5 | Self Declaration and evaluation during site visit
| A) Same Floor Staging area |  | 5
| B) Different floor staging area |  | 2
28 | The racks in cage area should be of 42U size with horizontal and vertical cable managers and the bidder to provide inter-rack cabling using patch panels, cross connects to communication area, cable managers for structured cabling, redundant power strips, earthing for each rack etc. |  |  | 2 | Self Declaration
29 | The bidder should be able to provide space in the same server hall contiguous to the existing cage area for addition of racks at the contracted rate during the period of contract. In case bidder decides to offer the space in contiguous area to some other customer, the first right of refusal would rest with LIC. |  |  | 2
| Total |  |  | 100
| FUEL/Generators | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
30 | Diesel Tanks (for generators) –It should have high capacity diesel tanks for ensuring 48 hour power backup with contracts for fuel supply on demand. |  |  | 5 | Self Declaration and evaluation during site visit
31 | The Diesel tanks should be underground. |  |  | 2
32 | Generators should be capable of providing power for 72 hours or continuously if fuel tanks are refilled |  |  | 5 | Self Declaration
33 | Critical Services like power, UPS Genset etc. are managed by: |  |  | 3 | Self Declaration and evaluation during site visit
a. | Own dedicated staff of the bidder |  | 3
b. | Maintenance services are Outsourced to third party |  | 2
34 | Number of Generators (>2) |  | 5 | 5 | Relavant Documents and evaluation during site visit
| Number of Generators (>1) |  | 2
| Total |  |  | 20
| POWER/UPS | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
35 | Two independent power suppliers/substations/Grid Level redundancy each capable of supporting the site independently. |  |  | 5 | Self Declaration and evaluation during site visit
36 | There should be sufficient power backups in places for running the Building Monitoring System in the event of power outage |  |  | 3 | Self Declaration
37 | The entire solution should be automatic with power supply from the transformer as the primary source and automatic switchover to DG set as a secondary source |  |  | 3 | Self Declaration and evaluation during site visit
38 | UPS should be configured in N+N redundancy mode. |  |  | 3 | Self Declaration
39 | Power of minimum 6 KVA per rack should be provided. Additional power if required to be made available |  |  | 5
40 | 32/63 amps power sockets will be made available by the Vendor if required |  |  | 3 | Self Declaration
41 | Power should be available from two different power sources |  |  | 3 | Self Declaration and evaluation during site visit
42 | Sufficient power supply at metered rate should be available to the proposed caged area |  |  | 5 | Self Declaration
43 | Data Center to maintain the PUE from 1.5 to 1.8. |  |  | 3 | Relavant Document to be attached
44 | Availability of 3 phase, 4 wire power system. |  |  | 3
45 | The Service Provider should provide the electrical cabling required by the racks to be hosted in the Data Center. |  |  | 3 | Self Declaration
46 | The service provider must make provision for a power meter to measure power consumption by the Corporation. |  |  | 3 | Self Declaration
47 | The service provider shall provide Dual meter for measuring the electricity units consumed by LIC for the Servers/Equipment. |  |  | 3
48 | The Switch over from one meter to the other should be automatic. i.e. Should coincide with switch over from normal power to generator power and vice versa. |  |  | 2
49 | Are the incoming utility feeds resilient incoming supplies from alternate power sub-stations arranged as N+1, each entering the site from diverse paths and each terminated in separate fire resistant enclosures? |  | 2 | 3 | Self Declaration and evaluation during site visit
| Does the utility power enter the site via false flooring/underground. |  | 1
50 | Each component must allow concurrent maintenance without disruption to supply of services to data halls or support areas. |  |  | 3 | Self Declaration
51 | Comprehensive Power Audit in the last two years / Record of past incidents |  |  | 2 | Relavant Documents to be attached
| Total |  |  | 55
| COOLING | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
52 | The design for cooling infrastructure at the Data Center should be in lines with standard guidelines to support high density cooling needs |  |  | 3 | Relavant Documents to be attached
53 | Redundant CRAC units to facilitate High Density cooling needs. |  |  | 2
54 | Chiller specification should be minimum of N+1 Water Cooled (Upgradable to 2N, Water-Cooled + Air-Cooled) |  |  | 3
55 | Water storage for cooling should be 36 hours at full load. |  |  | 3
56 | Chilled Water Distribution should be 2N, UPS powered. |  |  | 3
57 | The temperature in the server hall should be maintained at 21 +/- 2 °C |  |  | 2
58 | The humidity at the Data Center should be maintained at 50 % +/- 5% RH. |  |  | 2
59 | The server room should have precision air conditioning with redundancy |  |  | 2
| Total |  |  | 20
| FIRE | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
60 | The doors and walls for the server room, communications room, and other critical areas should be fire rated for a minimum 2 hrs. |  |  | 5 | Relavant Documents to be attached
61 | The false flooring in server hall should be fire resistant and tiles should be made up of Calcium Silicate. |  |  | 5
62 | Fire Protection specification should have VESDA, FM200/FE 227 Gas Suppression System, NOVEC 1230,Double Interlock Type Pre-Action Sprinkler System outside cage area. |  |  | 5
63 | Smoke detection and fire suppression for the building to be available where in the proposed Corporation’s cabin invariably covered under these systems |  |  | 5
64 | The proposed server room cabin area should be well covered in the fire detection and suppression (preferably inert gas based) system |  |  | 5
| Total |  |  | 25
| SECURITY | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
65 | Access card entry for the caged area |  |  | 5 | Self Declaration
66 | Biometric Access to the common entry to the Server room/ Server Hall area should be available |  |  | 5 | Relavant Documents and
67 | Access card entry for the cabin rack |  |  | 4 | Self Declaration
68 | Security for the building to be available 24x7x365 with security patrol and CCTV surveillance at the entry/Exit levels |  |  | 5 | Relavant Documents and evaluation during site visit
69 | 8 layers of physical access security checkpoints with anti-tailgating mantraps.Full details must be clearly mentioned by the bidder |  |  | 5 | Relavant Documents and evaluation during site visit
70 | The Data Center building should have impact resistant fence wall with intrusion detection & road blocking device. |  |  | 5 | Self Declaration and evaluation during site visit
71 | Activities to be recorded and the archival should be kept for at-least 2 years or for a longer period as per LIC’s Requirements |  |  | 3 | Relavant Documents and evaluation during site visit
72 | The CCTV Cameras should cover in row view of both front & back side of the racks row, within the Corporation’s server caged area. The CCTV camera should cover the entry & exit to the Corporation’s caged area. CCTV monitoring should cover all the blind spots within the caged area. |  |  | 5 | Self Declaration
73 | Dedicated feeds should be provided to Corporation for monitoring the cage/its infrastructure remotely |  |  | 3
74 | All the Building Management system (BMS) activities are to be controlled centrally in a room specifically to be used for BMS activities. The Vendor should manage the BMS activities on a 24x7x365 basis or as the Corporation decides |  |  | 5
75 | The proposed datacenter should have multi layers of physical security: |  |  | 5 | Self Declaration and evaluation during site visit
a. | Site Perimeter (Public Zone) |  | 1
b. | Perimeter Security (Reception 1 Zone) |  | 1
c. | Facility control (Operating Zone) |  | 1
d. | Server Hall (high security Zone) |  | 1
e. | Details of security arrangements in the Data Center to be submitted. |  | 1
| Total |  |  | 50
| NETWORK | Compliance (Yes/No) | Sub Group Weightage | Weightage | Supporting Documents Required | Details of Proof Attached
76 | Telecom junction box, multiplexers of various service providers to be available in and around the building |  |  | 5 | Self Declaration and evaluation during site visit
77 | The Data Center should be carrier neutral from the Telecom providers perspective. |  |  | 3
78 | Provision for multiple telecom carriers entry from diversified paths. |  |  | 3
79 | Provision for dual entrance room, local carrier room, meet-me room. |  |  | 3
80 | If the Telecom junction box, multiplexers of service provider from whom Corporation would be procuring the links is not available then the DC service provider should make necessary arrangements and allow the commissioning of the same |  |  | 5 | Self Declaration
81 | The co-hosting facility service provider should extend the link terminated by the link service provider on the junction box till the server room where the Corporation’s networking equipment will be located. |  |  | 2
82 | Data Center service provider should ensure fibers from multiple providers are fed to the site from three independent channels in ring connectivity. |  |  | 5
83 | 3 Redundant MPLS /Leased Line networks from 3 different providers must also be made available. |  |  | 5
84 | The service provider will be responsible for LAN cabling and providing mode of connectivity from cabin server room at co-location. |  |  | 3
85 | The entire cabling should be structured; service provider should provide the support for the same throughout the contract period. |  |  | 3
86 | Provision of cross connect irrespective of link service provider and bandwidth will be made available by co-location SP. |  |  | 3
87 | The cabling should be laid in a separate enclosure below the false floor and should be kept at a distance which does not cause Electro Magnetic induction with the power cabling. |  |  | 5
| Total |  |  | 45
*Note- Documentary Evidence must be furnished against each of the above criteria along with an index. All documents must be signed by the authorized signatory of the bidder. Relevant portions, in the documents submitted in pursuance of eligibility criteria, should be highlighted.
This is to certify that I have read and understood all instructions and requirements, and this hardcopy matches exactly with softcopy that is being submitted
| Signature of Vendor/Vendor's Representative | Date | 2019-08-07 10:55